## Site
GEOGRAPHICAL DATA
| Parameter | Value | Units | Description
1 | Latitude | 40.7 | Degree | Latitude of the location, positive in the Northern Hemisphere and negative in the Southern Hemisphere.
2 | Longitude | -3.7 | Degree | Longitude of the location, negative towards West and positive towards East.
3 | Altitude | 667 | Meter | Altitude of the location over sea level.
4 | StandardLongitude | 0 | Degree | Standard longitude (multiple of 15º). Negative towards West and positive towards East.

## Meteo
METEOROLOGICAL INPUT DATA
| Parameter | Value | Units | Description
1 | InputData | 1 |  | Meteorological input data
2 | TimeSeries | 1 |  | Synthetic method for generating the times series when monthly averages are selected as input data
3
4
5 | Month | Gdm0 [Wh/m2] | Tmm [ºC] | TMm [ºC] | Parameter
6 | January | 2080 | 3 | 10 | Gdm0 | Monthly average of daily global horizontal irradiation, Wh/m2
7 | February | 3130 | 3.1 | 12.7 | Tmm | Monthly average of minimum daily temperature, ºC.
8 | March | 4690 | 5.3 | 16.3 | TMm | Monthly average of maximum daily temperature, ºC.
9 | April | 5600 | 6.2 | 17.8
10 | May | 6640 | 10.2 | 22
11 | June | 7670 | 15.1 | 29
12 | July | 8030 | 17 | 31.7
13 | August | 7000 | 16.5 | 31.2
14 | September | 5370 | 13.3 | 26.1
15 | October | 3700 | 10.4 | 20.2
16 | November | 2390 | 6.1 | 13.3
17 | December | 1910 | 3.4 | 10

## PVgen
PV GENERATOR
| Parameter | Value | Units | Description
1 | PVnom | 5 | kWp | Nominal PV power
2 | CVPT | 0.5 | %·ºC-1 | Coefficient of Variation of PV module Power with Temperature (absolute value)
3 | NOCT | 48 | ºC | Nominal Operation Cell Temperature
4 | Rth | 0.035 | ºC·m2/W | Thermal resistance. This parameter is calculated as [NOCT-20]/800, but other values can be chosen depending on the mounting and ventilation of PV modules.
5 | Mounting structure
6 | Mounting | 1 |  | Type of mounting structure: static or solar tracker (horizontal, azimutal and two axis)
7
8 | Static ground or roof
9 | Inclination | 35 | Degree | Inclination of the modules regarding the horizontal, from 0º to 90º.
10 | Orientation | 0 | Degree | Orientation of the modules towards the Equator. Zero towards the South in the Northern Hemisphere (North in the Southern Hemisphere), negative towards the East, and positive towards the West.
11
12 | Static delta
13 | Inclination | 45 | Degree | Inclination of the modules regarding the horizontal, from 0º to 90º. The same for East and West structrures.
14
15 | Azimutal tracking
16 | Inclination | 40 | Degree | Inclination of the modules regarding the horizontal, from 0º to 90º.

## Inverter
Inverter
| Parameters | Value | Units | Description
1 | PInom | 4 | kW | Nominal output power of the inverter.
2 | PImax | 4 | kW | Maximum output power of the inverter.
3 | InverterCurve | 1 | - | Specification of the power efficiency curve
4 | Model parameters
5 | k0 | 0.01 | - | No-load inverter losses.
6 | k1 | 0.05 | - | Linear inverter losses.
7 | k2 | 0.08 | - | Joule inverter losses.
8 | Points of the power efficiency curve
9 | pac | Efficiency [%]
10 | 0 | 0
11 | 0.1 | 94.2
12 | 0.25 | 96.4
13 | 0.5 | 96.7
14 | 0.75 | 96.4
15 | 1 | 96.2

## Wiring
WIRING
| Parameter | Value | Units | Description
1 | WDC | 1 | % | DC wiring losses
2 | WAC | 1 | % | AC wiring losses

## Battery
BATTERY (Stand-alone PV systems)
| Parameter | Value | Units | Description
1 | CBAT | 150 | kWh | Battery capacity
2 | SOCmax | 1 | - | Maximum state of charge. The PV generator is disconnected when the SOC exceeds this value.
3 | SOCmin | 0 | - | Minimum state of charge. Inverter and loads are disconnected when SOC decreases below this value.

## Load
LOAD PROFILES
Monthly average of daily energy consumption, Ldm [kWh/day]
1 | Month | Ldm
2 | January | 50
3 | February | 50
4 | March | 50
5 | April | 50
6 | Mayo | 50
7 | June | 50
8 | July | 50
9 | August | 50
10 | September | 50
11 | October | 50
12 | November | 50
13 | December | 50
14 | Total | 18250 |  | Total yearly energy consumption [kWh/year]
15
16
17 | Normalised daily load profile
18
19 | Hour, h | F(h) |  | F(h) indicates the fraction of daily energy consumed during the hour h.
20 | 1 | 0.058 |  | (For a constant load profile write F(h)=1/24)
21 | 2 | 0.032
22 | 3 | 0.018 |  |  | Peak load demand | 7.2 | kW
23 | 4 | 0.015
24 | 5 | 0.014
25 | 6 | 0.018
26 | 7 | 0.034
27 | 8 | 0.03
28 | 9 | 0.019
29 | 10 | 0.017
30 | 11 | 0.018
31 | 12 | 0.021
32 | 13 | 0.027
33 | 14 | 0.031
34 | 15 | 0.036
35 | 16 | 0.052
36 | 17 | 0.051
37 | 18 | 0.036
38 | 19 | 0.025
39 | 20 | 0.024
40 | 21 | 0.045
41 | 22 | 0.117
42 | 23 | 0.144
43 | 24 | 0.118
| Total | 1 | (The sum of hourly fractions is correct)

## Genset
GENERATOR SET
| Parameter | Value | Units | Description
1 | PGENnom | 10 | kW | Nominal power of the genset
2 | SOCstart | 0.2 | - | State of charge for connecting the genset
3 | SOCstop | 0.3 | - | State of charge for disconnecting the genset
4
5 | Fuel consumption | Value | Units | Description
6 | b0i | 3.3672 | (l/h) | Intercept coefficient 0
7 | b1i | 0.02031 | (l/h)/kWnom | Intercept coefficient 1
8 | b0s | 0.25098 | (l/h)/kW | Slope coefficient 0
9 | b1s | -1.18e-05 | (l/h)/(kWnom·kW) | Slope coefficient 1
10
11 | Fuel consumption curve
12 | PGEN, [kW] | F [l/h]
13 | 0 | 3.5703
14 | 2.5 | 4.1974
15 | 5 | 4.8246
16 | 7.5 | 5.4518
17 | 10 | 6.0789

## Wind
Wind turbine
| Parameter | Value | Units | Description
1 | PWnom | 20 | kW | Rated electrical power
2 | Vnom | 10 | m/s | Rated wind speed
3 | Vci | 3 | m/s | Cut-in wind speed
4 | Vco | 15 | m/s | Cut-out wind speed
5 | Cpeq | 0.020555 | kW/(m/s)3 | Equivalent power coefficient (Cpeq=0,5·r·A·Cp)
6 | Power curve
7 | Wind speed, m/s | Power, kW
8 | 0 | 0
9 | 3 | 0
10 | 4.4 | 1.196
11 | 5.8 | 3.4555
12 | 7.2 | 7.1171
13 | 8.6 | 12.5191
14 | 10 | 20
15 | 15 | 20
16 | 15 | 0

## Pumping
WATER PUMPING
| Well/borehole | Value | Units | Description
1 | Hs | 12 | m | Static head
2 | Qtest | 5 | m3/h | Constant test flow
3 | Hdr | 2 | m | Drawdown at constant test flow
4 | kw1 | 0.4 | m/(m3/h) | Aquifer loss (this parameter is calculated as Hdr/Qtest, but other value can be chosen if a stepdrawdown test is available).
5 | kw2 | 0 | m/(m3/h)2 | Well loss (set to zero if only constant test flow is available).
6
7 | Water tank | Value | Units | Description
8 | WTC | 1000 | m3 | Water tank capacity (in this version the water storage is considered unlimited)
9 | Hr | 5 | m | Discharge level
10
11 | Pump | Value | Units | Description
12 | Qrated | 5 | m3/h | Rated flow
13 | Hrated | 16 | m | Rated head
14 | Density | 998.2 | kg/m3 | Liquid density
15
16 | System curve | Value | Units | Description
17 | HF,rated | 2 | m | Friction losses at rated flow Qrated
18 | ks0 | 17 | m | Total static head (Hs+Hr)
19 | ks1 | 0.4 | m/(m3/h) | Specific drawdown (aquifer loss)
20 | ks2 | 0.08 | m/(m3/h)2 | Friction plus well losses
21
22 | System curve
23 | Flow, Q [m3/h] | Head, H [m]
24 | 0 | 17
25 | 0.75 | 17.345
26 | 1.5 | 17.78
27 | 2.25 | 18.305
28 | 3 | 18.92
29 | 3.75 | 19.625
30 | 4.5 | 20.42
31 | 5.25 | 21.305
32 | 6 | 22.28
33 | 6.75 | 23.345
34
35 | Pump curve
36
37 | Q [m3/h] | H [m]
38 | 0.012 | 24.75
39 | 1.025 | 23.67
40 | 2.013 | 22.21
41 | 3.003 | 20.73
42 | 4.019 | 18.69
43 | 4.976 | 15.85
44 | 6.005 | 11.44
45
46
47
48
49 | Power curves
50 | P1, nominal curve of the power at the motor input, kW
51 | Q [m3/h] | P1 [kW]
52 | 0.012 | 0.253
53 | 1.025 | 0.336
54 | 2.013 | 0.414
55 | 3.003 | 0.481
56 | 4.019 | 0.53
57 | 4.976 | 0.553
58 | 6.005 | 0.549
59
60
61
62
63 | P2, nominal curve of shaft power, kW
64 | Q [m3/h] | P2 [kW]
65 | 0.012 | 0.098
66 | 1.025 | 0.176
67 | 2.013 | 0.248
68 | 3.003 | 0.309
69 | 4.019 | 0.352
70 | 4.976 | 0.371
71 | 6.005 | 0.368
72
73
74
75
76 | Motor | Value | Units | Description
77 | P2rated | 0.75 | kW | Rated shaft power
78 | RPMnom | 2900 | rpm | Rated speed
79 | RPMcool | 70 | % | Minimum speed, relative to the rated speed, for water cooling
80 | RPMmax | 120 | % | Maximum speed, relative to the rated speed
81
82 | Power efficiency
83 | P2 [kW] | Efficiency [%]
84 | 0 | 0
85 | 0.098 | 38.6
86 | 0.176 | 52.4
87 | 0.371 | 67.2
88 | 0.5 | 71
89 | 0.7 | 73
90 | 0.9 | 72
91

## Options
SIMULATION OPTIONS
| Parameter | Value | Units | Description
1 | Application | 1 | - | PV application
2 | Soiling and incidence losses | 1 | - | Degree of soiling on the PV generator under normal incidence
3 | Diffuse model | 2 | - | Diffuse sky model
4 | Diffuse fraction | 1 | - | Monthly diffuse fraction
5 | Ground reflectance | 0.2 | - | Ground reflectance
6 | Simulation step | 600 | s | Simulation step